|  |
| --- |
| **INAB ACCREDITED BUILDING AIRTIGHTNESS TEST & RESULTS** |
| **Report Number:** | **9788** |
| **Building Name & Address** | **18 Coach Close Ashbourne Co, Meath** |
| **Client Details:** | **Granbrind Ltd** |
| **Test Date:** | **17/04/2025** |
| **Test Time:** | **14:37:00** | **DEAP Value:** |
| **Test Engineer:** | **Charles McCullagh** | **RESULTS**  |
| **Tester position:** | **Inside** |
| **Building Measurements**  |  |
| **Volume, *V*:** | **447.00 m³** | **Air changes at 50 Pa, n50 [/h]:** | **2.56** |
| **Envelope Area, *Ae*:** | **408.00 m²** | **Air Permeability at 50 Pa, AP50:** | **2.810209m3.h-1.m-2** |
| **Floor Area, *Af*::** | **172.46 m²** | **Flow per Floor Area at 50 Pa, [m³/h/m²]:** | **6.64** |
|  | **Air flow at 50 Pa, [h/m²]:** | **1146.56** |
|  | **Correlation Coefficient, r2:** | **0.99885** |
|  | **Slope, n:** | **0.500214931** |
|  | **Air Flow Coefficient, Cenv:** | **159.87 m3.h-1** |
|  | **Air Leakage Coefficient, CL:** | **162.01 m3.h-1** |
| **The Building achieved an air permeability of 2.810209 m3.h-1.m-2 This is Less than the specified air permeability of 3 m3.h-1.m-2 at 50 Pa building pressure** |
| **Test Data** | **Depressurized or Pressurized Method 2**  |
| **Start (Pa):** | **1.10** | **1.20** | **1.30** | **Start Inside Temperature** | **14.0°C** | **Start Outside Temperature** | **8.0°C** |
| **Building (Pa)** | **-25.00** | **-30.00** | **-35.00** | **-40.00** | **-45.00** | **-50.00** | **-55.00** | **-60.00** |
| **Flow** | **1272.00** | **1207.00** | **1153.00** | **1091.00** | **1015.00** | **949.00** | **893.00** | **810.00** |
| **Error** | **0.8** | **-0.1** | **0.2** | **0.0** | **-1.2** | **-1.0** | **0.8** | **0.5** |
| **End (Pa):** |  |  |  | **End Inside Temperature** | **14.0°C** | **End Outside Temperature** | **8.0°C** |
| **Average Barometric Pressure** | **99.8 kPa** | **Wind Speed** |  |

|  |  |  |
| --- | --- | --- |
| ***Graph of Building Pressure*** |  | ***Equipment details used in test*** |
|  |  | **Equipment Type** | **Serial No……** | **22/11/2019** |
|  | **#7 Fan:** | **3XLF01818** |  |
|  | **Manometer:** |  |  |
|  | **Barometer:** |  |  |
|  | **Thermometer:** |  |  |
| ***Information of building*** |
| **Type of Test:** | **Whole Building** |
| **Internal Doors:** | **Open** |
| **External Doors:** | **Closed** |
| **External Windows:** | **Closed** |
| **Trickle Vents:** | **Closed & Sealed** |
| **Ventilation:** | **Continuous mechanical ventilation (CMEV)** | **Sealed** |
| **Heating:** | **Gas/Oil/Heap Pump** |
| **Deviations from Standard’s Notes:** |
| ***The building has been tested in accordance with the following standards. EN ISO 9972:2015, ATTMA TSL1/TLS2/TSL3 and BCTS Ltd ISO17025 quality management system. Refer to terms and condition for MU. The external envelope was calculated by BCTS from drawings issued by the client.***  |
|
| **Checked by and signed off by:** | **Brian Cunningham:**  | **Director.** | **Date:** |