|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **INAB ACCREDITED BUILDING AIRTIGHTNESS TEST & RESULTS** | | | | | | | | | | | | | | | |
| **Report Number:** | | | | | **3313** | | | | | | | | | | |
| **Building Name & Address** | | | | | **Site\_13 13 Thornhill Oaks, Cherrygarth, Mount Merrion, Dublin** | | | | | | | | | | |
| **Client Details:** | | | | | **Adston Construction** | | | | | | | | | | |
| **Test Date:** | | | | | **31/03/2023** | | | | | | | | | | |
| **Test Time:** | | | | | **08:59:00** | | | | | | | **DEAP Value:** | | | |
| **Test Engineer:** | | | | | **Brian P Cunningham** | | | | | | | **RESULTS** | | | |
| **Tester position:** | | | | | **Inside** | | | | | | |
| **Building Measurements** | | | | |  | | | | | | |
| **Volume, *V*:** | | **232.00 m³** | | | **Air changes at 50 Pa, n50 [/h]:** | | | | | | | **3.18** | | | |
| **Envelope Area, *Ae*:** | | **284.00 m²** | | | **Air Permeability at 50 Pa, AP50:** | | | | | | | **2.603041m3.h-1.m-2** | | | |
| **Floor Area, *Af*::** | | **86.00 m²** | | | **Flow per Floor Area at 50 Pa, [m³/h/m²]:** | | | | | | | **8.59** | | | |
|  | | | | | **Air flow at 50 Pa, [h/m²]:** | | | | | | | **739.26** | | | |
|  | | | | | **Correlation Coefficient, r2:** | | | | | | | **0.99503** | | | |
|  | | | | | **Slope, n:** | | | | | | | **0.709300992** | | | |
|  | | | | | **Air Flow Coefficient, Cenv:** | | | | | | | **45.50 m3.h-1** | | | |
|  | | | | | **Air Leakage Coefficient, CL:** | | | | | | | **46.10 m3.h-1** | | | |
| **The Building achieved an air permeability of 2.603041 m3.h-1.m-2 This is Less than the specified air permeability of 3 m3.h-1.m-2 at 50 Pa building pressure** | | | | | | | | | | | | | | | |
| **Test Data** | | | | | | **Depressurized or Pressurized Method 2** | | | | | | | | | |
| **Start (Pa):** | **1.10** | | **1.20** | **1.30** | **Start Inside Temperature** | | | | **8.9°C** | **Start Outside Temperature** | | | | | **8.3°C** |
| **Building (Pa)** | **-25.00** | | **-30.00** | | **-35.00** | | **-40.00** | **-45.00** | | | **-50.00** | **-55.00** | | **-60.00** | |
| **Flow** | **845.00** | | **788.00** | | **752.00** | | **701.00** | **621.00** | | | **592.00** | **533.00** | | **441.00** | |
| **Error** | **-0.5** | | **-1.3** | | **0.8** | | **1.3** | **-2.4** | | | **2.4** | **2.9** | | **-3.0** | |
| **End (Pa):** |  | |  |  | **End Inside Temperature** | | | | **8.9°C** | | **End Outside Temperature** | | | | **8.3°C** |
| **Average Barometric Pressure** | | | | **101.72 kPa** | | | | | **Wind Speed** | | | |  | | |

|  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ***Graph of Building Pressure*** | |  | ***Equipment details used in test*** | | | | | |
|  | |  | **Equipment Type** | | | **Serial No……** | **18/02/2022** | |
|  | **#6 Fan:** | | | **3XLFT00458** |  | |
|  | **Manometer:** | | |  |  | |
|  | **Barometer:** | | |  |  | |
|  | **Thermometer:** | | |  |  | |
| ***Information of building*** | | | | | | |
| **Type of Test:** | | **Whole Building** | | | | |
| **Internal Doors:** | | **Open** | | | | |
| **External Doors:** | | **Closed** | | | | |
| **External Windows:** | | **Closed** | | | | |
| **Trickle Vents:** | | **Closed & Sealed** | | | | |
| **Ventilation:** | | **System 3 - Continuous Mechanical Extraction** | | | | **Sealed** |
| **Heating:** | | **Gas/Oil/Heap Pump** | | | | |
| **Deviations from Standard’s Notes:** | | | | | | |
| ***The building has been tested in accordance with the following standards. EN ISO 9972:2015, ATTMA TSL1/TLS2/TSL3 and BCTS Ltd ISO17025 quality management system. Refer to terms and condition for MU. The external envelope was calculated by BCTS from drawings issued by the client.*** | | | | | | | | |
|
| **Checked by and signed off by:** | **Brian Cunningham:** | | | | **Director.** | **Date:** | | |