|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **INAB ACCREDITED BUILDING AIRTIGHTNESS TEST & RESULTS** | | | | | | | | | | | | | | | |
| **Report Number:** | | | | | **9371** | | | | | | | | | | |
| **Building Name & Address** | | | | | **Apartment 1 Ballygossan Hill, Skerries** | | | | | | | | | | |
| **Client Details:** | | | | | **Twinlite** | | | | | | | | | | |
| **Test Date:** | | | | | **11/03/2025** | | | | | | | | | | |
| **Test Time:** | | | | | **12:18:00** | | | | | | | **DEAP Value:** | | | |
| **Test Engineer:** | | | | | **Brian P Cunningham** | | | | | | | **RESULTS** | | | |
| **Tester position:** | | | | | **Inside** | | | | | | |
| **Building Measurements** | | | | |  | | | | | | |
| **Volume, *V*:** | | **267.00 m³** | | | **Air changes at 50 Pa, n50 [/h]:** | | | | | | | **1.79** | | | |
| **Envelope Area, *Ae*:** | | **292.00 m²** | | | **Air Permeability at 50 Pa, AP50:** | | | | | | | **1.643518m3.h-1.m-2** | | | |
| **Floor Area, *Af*::** | | **90.16 m²** | | | **Flow per Floor Area at 50 Pa, [m³/h/m²]:** | | | | | | | **5.32** | | | |
|  | | | | | **Air flow at 50 Pa, [h/m²]:** | | | | | | | **479.90** | | | |
|  | | | | | **Correlation Coefficient, r2:** | | | | | | | **0.37051** | | | |
|  | | | | | **Slope, n:** | | | | | | | **0.477928876** | | | |
|  | | | | | **Air Flow Coefficient, Cenv:** | | | | | | | **72.67 m3.h-1** | | | |
|  | | | | | **Air Leakage Coefficient, CL:** | | | | | | | **73.98 m3.h-1** | | | |
| **The Building achieved an air permeability of 1.643518 m3.h-1.m-2 This is Less than the specified air permeability of 3 m3.h-1.m-2 at 50 Pa building pressure** | | | | | | | | | | | | | | | |
| **Test Data** | | | | | | **Depressurized or Pressurized Method 2** | | | | | | | | | |
| **Start (Pa):** | **1.10** | | **1.20** | **1.30** | **Start Inside Temperature** | | | | **12.0°C** | **Start Outside Temperature** | | | | | **10.0°C** |
| **Building (Pa)** | **-25.00** | | **-30.00** | | **-35.00** | | **-40.00** | **-45.00** | | | **-50.00** | **-55.00** | | **-60.00** | |
| **Flow** | **677.00** | | **620.00** | | **589.00** | | **262.00** | **224.00** | | | **483.00** | **439.00** | | **405.00** | |
| **Error** | **29.5** | | **23.8** | | **23.1** | | **-42.4** | **-47.8** | | | **20.2** | **17.8** | | **18.9** | |
| **End (Pa):** |  | |  |  | **End Inside Temperature** | | | | **12.0°C** | | **End Outside Temperature** | | | | **10.0°C** |
| **Average Barometric Pressure** | | | | **101.28 kPa** | | | | | **Wind Speed** | | | |  | | |

|  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ***Graph of Building Pressure*** | |  | ***Equipment details used in test*** | | | | | |
|  | |  | **Equipment Type** | | | **Serial No……** | **18/02/2022** | |
|  | **#6 Fan:** | | | **3XLFT00458** |  | |
|  | **Manometer:** | | |  |  | |
|  | **Barometer:** | | |  |  | |
|  | **Thermometer:** | | |  |  | |
| ***Information of building*** | | | | | | |
| **Type of Test:** | | **Whole Building** | | | | |
| **Internal Doors:** | | **Open** | | | | |
| **External Doors:** | | **Closed** | | | | |
| **External Windows:** | | **Closed** | | | | |
| **Trickle Vents:** | | **Closed & Sealed** | | | | |
| **Ventilation:** | | **Continuous mechanical ventilation (CMEV)** | | | | **Sealed** |
| **Heating:** | | **Gas/Oil/Heap Pump** | | | | |
| **Deviations from Standard’s Notes:** | | | | | | |
| ***The building has been tested in accordance with the following standards. EN ISO 9972:2015, ATTMA TSL1/TLS2/TSL3 and BCTS Ltd ISO17025 quality management system. Refer to terms and condition for MU. The external envelope was calculated by BCTS from drawings issued by the client.*** | | | | | | | | |
|
| **Checked by and signed off by:** | **Brian Cunningham:** | | | | **Director.** | **Date:** | | |