|  |
| --- |
| **INAB ACCREDITED BUILDING AIRTIGHTNESS TEST & RESULTS** |
| **Report Number:** | **8878** |
| **Building Name & Address** | **2 Storey, Modular Portlaoise College** |
| **Client Details:** | **ABM, Design and Build** |
| **Test Date:** | **02/12/2024** |
| **Test Time:** | **13:10:00** | **DEAP Value:** |
| **Test Engineer:** | **Raymond Mc Kenna** | **RESULTS**  |
| **Tester position:** | **Inside** |
| **Building Measurements**  |  |
| **Volume, *V*:** | **3375.00 m³** | **Air changes at 50 Pa, n50 [/h]:** | **1.69** |
| **Envelope Area, *Ae*:** | **1782.00 m²** | **Air Permeability at 50 Pa, AP50:** | **3.213906m3.h-1.m-2** |
| **Floor Area, *Af*::** | **482.00 m²** | **Flow per Floor Area at 50 Pa, [m³/h/m²]:** | **11.88** |
|  | **Air flow at 50 Pa, [h/m²]:** | **5727.18** |
|  | **Correlation Coefficient, r2:** | **0.99356** |
|  | **Slope, n:** | **0.58965857** |
|  | **Air Flow Coefficient, Cenv:** | **560.35 m3.h-1** |
|  | **Air Leakage Coefficient, CL:** | **570.33 m3.h-1** |
| **The Building achieved an air permeability of 3.213906 m3.h-1.m-2 This is Less than the specified air permeability of 3 m3.h-1.m-2 at 50 Pa building pressure** |
| **Test Data** | **Depressurized or Pressurized Method 2**  |
| **Start (Pa):** | **1.10** | **1.20** | **1.30** | **Start Inside Temperature** | **12.8°C** | **Start Outside Temperature** | **7.0°C** |
| **Building (Pa)** | **-25.00** | **-30.00** | **-35.00** | **-40.00** | **-45.00** | **-50.00** | **-55.00** | **-60.00** |
| **Flow** | **6234.00** | **5987.00** | **5653.00** | **5453.00** | **4938.00** | **4625.00** | **4243.00** | **3547.00** |
| **Error** | **-1.8** | **-0.6** | **-0.5** | **2.5** | **-0.2** | **1.6** | **2.7** | **-3.6** |
| **End (Pa):** |  |  |  | **End Inside Temperature** | **12.8°C** | **End Outside Temperature** | **7.0°C** |
| **Average Barometric Pressure** | **101.09 kPa** | **Wind Speed** |  |

|  |  |  |
| --- | --- | --- |
| ***Graph of Building Pressure*** |  | ***Equipment details used in test*** |
|  |  | **Equipment Type** | **Serial No……** | **20/04/2028** |
|  | **#14 Fan:** | **3PH603382** |  |
|  | **Manometer:** |  |  |
|  | **Barometer:** |  |  |
|  | **Thermometer:** |  |  |
| ***Information of building*** |
| **Type of Test:** | **Whole Building** |
| **Internal Doors:** | **Open** |
| **External Doors:** | **Closed** |
| **External Windows:** | **Closed** |
| **Trickle Vents:** | **Closed & Sealed** |
| **Ventilation:** |  | **Sealed** |
| **Heating:** | **Gas/Oil/Heap Pump** |
| **Deviations from Standard’s Notes:** |
| ***The building has been tested in accordance with the following standards. EN ISO 9972:2015, ATTMA TSL1/TLS2/TSL3 and BCTS Ltd ISO17025 quality management system. Refer to terms and condition for MU. The external envelope was calculated by BCTS from drawings issued by the client.***  |
|
| **Checked by and signed off by:** | **Brian Cunningham:**  | **Director.** | **Date:** |