|  |
| --- |
| **INAB ACCREDITED BUILDING AIRTIGHTNESS TEST & RESULTS** |
| **Report Number:** | **3971** |
| **Building Name & Address** | **147 Meadowbrook, Tullygally, Craigavon** |
| **Client Details:** | **IRS Scotland** |
| **Test Date:** | **22/05/2023** |
| **Test Time:** | **11:38:00** | **DEAP Value:** |
| **Test Engineer:** | **Brian P Cunningham** | **RESULTS**  |
| **Tester position:** | **Inside** |
| **Building Measurements**  |  |
| **Volume, *V*:** | **0.00 m³** | **Air changes at 50 Pa, n50 [/h]:** | **0.00** |
| **Envelope Area, *Ae*:** | **216.48 m²** | **Air Permeability at 50 Pa, AP50:** | **11.28417m3.h-1.m-2** |
| **Floor Area, *Af*::** | **0.00 m²** | **Flow per Floor Area at 50 Pa, [m³/h/m²]:** | **0.00** |
|  | **Air flow at 50 Pa, [h/m²]:** | **2442.79** |
|  | **Correlation Coefficient, r2:** | **0.99964** |
|  | **Slope, n:** | **0.65862204** |
|  | **Air Flow Coefficient, Cenv:** | **183.35 m3.h-1** |
|  | **Air Leakage Coefficient, CL:** | **185.74 m3.h-1** |
| **The Building achieved an air permeability of 11.28417 m3.h-1.m-2 This is Less than the specified air permeability of 0 m3.h-1.m-2 at 50 Pa building pressure** |
| **Test Data** | **Depressurized or Pressurized Method 2**  |
| **Start (Pa):** | **1.10** | **1.20** | **1.30** | **Start Inside Temperature** | **15.8°C** | **Start Outside Temperature** | **12.4°C** |
| **Building (Pa)** | **-25.00** | **-30.00** | **-35.00** | **-40.00** | **-45.00** | **-50.00** | **-55.00** | **-60.00** |
| **Flow** | **2806.00** | **2630.00** | **2470.00** | **2288.00** | **2129.00** | **1933.00** | **1764.00** | **1568.00** |
| **Error** | **0.7** | **0.0** | **0.0** | **-0.6** | **0.0** | **-0.8** | **0.2** | **0.6** |
| **End (Pa):** |  |  |  | **End Inside Temperature** | **15.8°C** | **End Outside Temperature** | **12.4°C** |
| **Average Barometric Pressure** | **102.51 kPa** | **Wind Speed** |  |

|  |  |  |
| --- | --- | --- |
| ***Graph of Building Pressure*** |  | ***Equipment details used in test*** |
|  |  | **Equipment Type** | **Serial No……** | **22/08/2022** |
|  | **#5 Fan:** | **5FN202443** |  |
|  | **Manometer:** |  |  |
|  | **Barometer:** |  |  |
|  | **Thermometer:** |  |  |
| ***Information of building*** |
| **Type of Test:** | **Whole Building** |
| **Internal Doors:** | **Open** |
| **External Doors:** | **Closed** |
| **External Windows:** | **Closed** |
| **Trickle Vents:** | **Closed & Sealed** |
| **Ventilation:** | **System 1 - Background ventilators and intermittent extractors** | **Sealed** |
| **Heating:** | **Gas/Oil/Heap Pump** |
| **Deviations from Standard’s Notes:** |
| ***The building has been tested in accordance with the following standards. EN ISO 9972:2015, ATTMA TSL1/TLS2/TSL3 and BCTS Ltd ISO17025 quality management system. Refer to terms and condition for MU. The external envelope was calculated by BCTS from drawings issued by the client.***  |
|
| **Checked by and signed off by:** | **Brian Cunningham:**  | **Director.** | **Date:** |