| INAB ACCREDITED BUILDING AIRTIGHTNESS TEST & RESULTS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Report Number: |  |  |  |  | 12909 |  |  |  |  |  |  |  |  |  |  |
| Building Name & Address |  |  |  |  | Site_42 Listoke Wood Ballymakenny Drogheda |  |  |  |  |  |  |  |  |  |  |
| Client Details: |  |  |  |  | Meegan Builders (Castleblayney) Ltd |  |  |  |  |  |  |  |  |  |  |
| Test Date: |  |  |  |  | 18/02/2026 |  |  |  |  |  |  |  |  |  |  |
| Test Time: |  |  |  |  | 09:19:00 |  |  |  |  |  |  | DEAP Value: |  |  |  |
| Test Engineer: |  |  |  |  | Brian P Cunningham |  |  |  |  |  |  | RESULTS |  |  |  |
| Tester position: |  |  |  |  | Inside |  |  |  |  |  |  |  |  |  |  |
| Building Measurements |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Volume, V: |  | 345.00 m³ |  |  | Air changes at 50 Pa, n50 [/h]: |  |  |  |  |  |  | 2.71 |  |  |  |
| Envelope Area, Ae: |  | 319.00 m² |  |  | Air Permeability at 50 Pa, AP50: |  |  |  |  |  |  | 2.935267m3.h-1.m-2 |  |  |  |
| Floor Area, Af:: |  | 128.19 m² |  |  | Flow per Floor Area at 50 Pa, [m³/h/m²]: |  |  |  |  |  |  | 7.30 |  |  |  |
|  |  |  |  |  | Air flow at 50 Pa, [h/m²]: |  |  |  |  |  |  | 936.35 |  |  |  |
|  |  |  |  |  | Correlation Coefficient, r2: |  |  |  |  |  |  | 0.97878 |  |  |  |
|  |  |  |  |  | Slope, n: |  |  |  |  |  |  | 0.517895024 |  |  |  |
|  |  |  |  |  | Air Flow Coefficient, Cenv: |  |  |  |  |  |  | 121.84 m3.h-1 |  |  |  |
|  |  |  |  |  | Air Leakage Coefficient, CL: |  |  |  |  |  |  | 123.46 m3.h-1 |  |  |  |
| The Building achieved an air permeability of 2.935267 m3.h-1.m-2 This is Less than the specified air permeability of 3 m3.h-1.m-2 at 50 Pa building pressure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test Data |  |  |  |  |  | Depressurized or Pressurized Method 2 |  |  |  |  |  |  |  |  |  |
| Start (Pa): | 1.10 |  | 1.20 | 1.30 | Start Inside Temperature |  |  |  | 4.0°C | Start Outside Temperature |  |  |  |  | 3.0°C |
| Building (Pa) | -25.00 |  | -30.00 |  | -35.00 |  | -40.00 | -45.00 |  |  | -50.00 | -55.00 |  | -60.00 |  |
| Flow | 995.00 |  | 948.00 |  | 992.00 |  | 844.00 | 790.00 |  |  | 738.00 | 684.00 |  | 631.00 |  |
| Error | -1.5 |  | -1.6 |  | 8.5 |  | -2.2 | -2.3 |  |  | -1.7 | -0.6 |  | 1.8 |  |
| End (Pa): |  |  |  |  | End Inside Temperature |  |  |  | 4.0°C |  | End Outside Temperature |  |  |  | 3.0°C |
| Average Barometric Pressure |  |  |  | 98.1 kPa |  |  |  |  | Wind Speed |  |  |  |  |  |  |

| Graph of Building Pressure |  |  | Equipment details used in test |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Equipment Type |  |  | Serial No…… | 18/02/2022 |  |
|  |  |  | #6 Fan: |  |  | 3XLFT00458 |  |  |
|  |  |  | Manometer: |  |  |  |  |  |
|  |  |  | Barometer: |  |  |  |  |  |
|  |  |  | Thermometer: |  |  |  |  |  |
|  |  | Information of building |  |  |  |  |  |  |
|  |  | Type of Test: |  |  |  |  |  |  |
|  |  | Internal Doors: |  | Open |  |  |  |  |
|  |  | External Doors: |  | Closed |  |  |  |  |
|  |  | External Windows: |  | Closed |  |  |  |  |
|  |  | Trickle Vents: |  | Closed & Sealed |  |  |  |  |
|  |  | Ventilation: |  | Continuous mechanical ventilation (CMEV) |  |  |  | Sealed |
|  |  | Heating: |  | Gas/Oil/Heap Pump |  |  |  |  |
|  |  | Deviations from Standard’s Notes: |  |  |  |  |  |  |
| The building has been tested in accordance with the following standards. EN ISO 9972:2015, ATTMA TSL1/TLS2/TSL3 and BCTS Ltd ISO17025 quality management system. Refer to terms and condition for MU. The external envelope was calculated by BCTS from drawings issued by the client. |  |  |  |  |  |  |  |  |
| Checked by and signed off by: | Brian Cunningham: |  |  |  | Director. | Date: |  |  |