| INAB ACCREDITED BUILDING AIRTIGHTNESS TEST & RESULTS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Report Number: |  |  |  |  | 2673 |  |  |  |  |  |  |  |  |  |  |
| Building Name & Address |  |  |  |  | Site_110 Coill Darrach Castleblayney Monaghan |  |  |  |  |  |  |  |  |  |  |
| Client Details: |  |  |  |  | Geda Construction |  |  |  |  |  |  |  |  |  |  |
| Test Date: |  |  |  |  | 10/01/2023 |  |  |  |  |  |  |  |  |  |  |
| Test Time: |  |  |  |  | 11:35:00 |  |  |  |  |  |  | DEAP Value: |  |  |  |
| Test Engineer: |  |  |  |  | Brian P Cunningham |  |  |  |  |  |  | RESULTS |  |  |  |
| Tester position: |  |  |  |  | Inside |  |  |  |  |  |  |  |  |  |  |
| Building Measurements |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Volume, V: |  | 235.90 m³ |  |  | Air changes at 50 Pa, n50 [/h]: |  |  |  |  |  |  | 1.22 |  |  |  |
| Envelope Area, Ae: |  | 258.84 m² |  |  | Air Permeability at 50 Pa, AP50: |  |  |  |  |  |  | 1.11501m3.h-1.m-2 |  |  |  |
| Floor Area, Af:: |  | 106.49 m² |  |  | Flow per Floor Area at 50 Pa, [m³/h/m²]: |  |  |  |  |  |  | 288.61 |  |  |  |
|  |  |  |  |  | Air flow at 50 Pa, [h/m²]: |  |  |  |  |  |  | 288.61 |  |  |  |
|  |  |  |  |  | Correlation Coefficient, r2: |  |  |  |  |  |  | 0.99769 |  |  |  |
|  |  |  |  |  | Slope, n: |  |  |  |  |  |  | 0.608725624 |  |  |  |
|  |  |  |  |  | Air Flow Coefficient, Cenv: |  |  |  |  |  |  | 26.52 m3.h-1 |  |  |  |
|  |  |  |  |  | Air Leakage Coefficient, CL: |  |  |  |  |  |  | 26.67 m3.h-1 |  |  |  |
| The Building achieved an air permeability of 1.11501 m3.h-1.m-2 This is Less than the specified air permeability of 0 m3.h-1.m-2 at 50 Pa building pressure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test Data |  |  |  |  |  | Depressurized or Pressurized Method 2 |  |  |  |  |  |  |  |  |  |
| Start (Pa): | 1.10 |  | 1.20 | 1.30 | Start Inside Temperature |  |  |  | 8.0°C | Start Outside Temperature |  |  |  |  | 6.4°C |
| Building (Pa) | -56.85 |  | -51.85 |  | -46.85 |  | -41.85 | -36.85 |  |  | -31.85 | -26.85 |  | -21.85 |  |
| Flow | 176.00 |  | 200.00 |  | 222.00 |  | 241.00 | 255.00 |  |  | 274.00 | 301.00 |  | 319.00 |  |
| Error | 0.3 |  | 0.5 |  | 0.6 |  | -0.1 | -2.2 |  |  | -1.9 | 1.3 |  | 1.6 |  |
| End (Pa): |  |  |  |  | End Inside Temperature |  |  |  | 8.0°C |  | End Outside Temperature |  |  |  | 6.4°C |
| Average Barometric Pressure |  |  |  | 98.03 kPa |  |  |  |  | Wind Speed |  |  |  |  |  |  |

| Graph of Building Pressure |  |  | Equipment details used in test |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Equipment Type |  |  | Serial No…… | 22/08/2022 |  |
|  |  |  | #5 Fan: |  |  | 5FN202443 |  |  |
|  |  |  | Manometer: |  |  |  |  |  |
|  |  |  | Barometer: |  |  |  |  |  |
|  |  |  | Thermometer: |  |  |  |  |  |
|  |  | Information of building |  |  |  |  |  |  |
|  |  | Type of Test: |  | Whole Building |  |  |  |  |
|  |  | Internal Doors: |  | Open |  |  |  |  |
|  |  | External Doors: |  | Closed |  |  |  |  |
|  |  | External Windows: |  | Closed |  |  |  |  |
|  |  | Trickle Vents: |  | Closed & Sealed |  |  |  |  |
|  |  | Ventilation: |  | System 3 - Continuous Mechanical Extraction |  |  |  | Sealed |
|  |  | Heating: |  | Gas/Oil/Heap Pump |  |  |  |  |
|  |  | Deviations from Standard’s Notes: |  |  |  |  |  |  |
| The building has been tested in accordance with the following standards. EN ISO 9972:2015, ATTMA TSL1/TLS2/TSL3 and BCTS Ltd ISO17025 quality management system. Refer to terms and condition for MU. The external envelope was calculated by BCTS from drawings issued by the client. |  |  |  |  |  |  |  |  |
| Checked by and signed off by: | Brian Cunningham: |  |  |  | Director. | Date: |  |  |