| INAB ACCREDITED BUILDING AIRTIGHTNESS TEST & RESULTS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Report Number: |  |  |  |  | 2481 |  |  |  |  |  |  |  |  |  |  |
| Building Name & Address |  |  |  |  | Site_7 Listoke Elms, Ballymakenny Road, Drogheda |  |  |  |  |  |  |  |  |  |  |
| Client Details: |  |  |  |  | Meegan Builders (Castleblayney) Ltd |  |  |  |  |  |  |  |  |  |  |
| Test Date: |  |  |  |  | 05/12/2022 |  |  |  |  |  |  |  |  |  |  |
| Test Time: |  |  |  |  | 11:14:00 |  |  |  |  |  |  | DEAP Value: |  |  |  |
| Test Engineer: |  |  |  |  | Brian P Cunningham |  |  |  |  |  |  | RESULTS |  |  |  |
| Tester position: |  |  |  |  | Inside |  |  |  |  |  |  |  |  |  |  |
| Building Measurements |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Volume, V: |  | 300.00 m³ |  |  | Air changes at 50 Pa, n50 [/h]: |  |  |  |  |  |  | 2.64 |  |  |  |
| Envelope Area, Ae: |  | 290.00 m² |  |  | Air Permeability at 50 Pa, AP50: |  |  |  |  |  |  | 2.73914m3.h-1.m-2 |  |  |  |
| Floor Area, Af:: |  | 113.00 m² |  |  | Flow per Floor Area at 50 Pa, [m³/h/m²]: |  |  |  |  |  |  | 794.35 |  |  |  |
|  |  |  |  |  | Air flow at 50 Pa, [h/m²]: |  |  |  |  |  |  | 794.35 |  |  |  |
|  |  |  |  |  | Correlation Coefficient, r2: |  |  |  |  |  |  | 0.99927 |  |  |  |
|  |  |  |  |  | Slope, n: |  |  |  |  |  |  | 0.771138676 |  |  |  |
|  |  |  |  |  | Air Flow Coefficient, Cenv: |  |  |  |  |  |  | 38.39 m3.h-1 |  |  |  |
|  |  |  |  |  | Air Leakage Coefficient, CL: |  |  |  |  |  |  | 38.89 m3.h-1 |  |  |  |
| The Building achieved an air permeability of 2.73914 m3.h-1.m-2 This is Less than the specified air permeability of 3 m3.h-1.m-2 at 50 Pa building pressure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test Data |  |  |  |  |  | Depressurized or Pressurized Method 2 |  |  |  |  |  |  |  |  |  |
| Start (Pa): | 1.10 |  | 1.20 | 1.30 | Start Inside Temperature |  |  |  | 10.2°C | Start Outside Temperature |  |  |  |  | 7.0°C |
| Building (Pa) | -57.65 |  | -52.65 |  | -47.65 |  | -42.65 | -37.65 |  |  | -32.65 | -27.65 |  | -22.65 |  |
| Flow | 435.00 |  | 519.00 |  | 588.00 |  | 664.00 | 717.00 |  |  | 779.00 | 842.00 |  | 905.00 |  |
| Error | -1.4 |  | 0.8 |  | 0.5 |  | 1.7 | -0.3 |  |  | -0.5 | -0.4 |  | -0.2 |  |
| End (Pa): |  |  |  |  | End Inside Temperature |  |  |  | 10.2°C |  | End Outside Temperature |  |  |  | 7.0°C |
| Average Barometric Pressure |  |  |  | 102.39 kPa |  |  |  |  | Wind Speed |  |  |  |  |  |  |

| Graph of Building Pressure |  |  | Equipment details used in test |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Equipment Type |  |  | Serial No…… | 16/08/2022 |  |
|  |  |  | #1 Fan: |  |  | 3PH600642 |  |  |
|  |  |  | Manometer: |  |  |  |  |  |
|  |  |  | Barometer: |  |  |  |  |  |
|  |  |  | Thermometer: |  |  |  |  |  |
|  |  | Information of building |  |  |  |  |  |  |
|  |  | Type of Test: |  | Whole Building |  |  |  |  |
|  |  | Internal Doors: |  | Open |  |  |  |  |
|  |  | External Doors: |  | Closed |  |  |  |  |
|  |  | External Windows: |  | Closed |  |  |  |  |
|  |  | Trickle Vents: |  | Closed & Sealed |  |  |  |  |
|  |  | Ventilation: |  | System 3 - Continuous Mechanical Extraction |  |  |  | Sealed |
|  |  | Heating: |  | Gas/Oil/Heap Pump |  |  |  |  |
|  |  | Deviations from Standard’s Notes: |  |  |  |  |  |  |
| The building has been tested in accordance with the following standards. EN ISO 9972:2015, ATTMA TSL1/TLS2/TSL3 and BCTS Ltd ISO17025 quality management system. Refer to terms and condition for MU. The external envelope was calculated by BCTS from drawings issued by the client. |  |  |  |  |  |  |  |  |
| Checked by and signed off by: | Brian Cunningham: |  |  |  | Director. | Date: |  |  |